COMPLIANCE SHEET TO BE FILLED IN BY THE CANDIDATE

#### 1) Medium Voltage Cable PRYSMIAN PROTOLON (SMK)-LWL (N)TSKCGEWOEU 3x25mm2+2x25mm2/2+1(6LWL) 12/20KV*

| Cable Specifications |  | Compliance (YES/NO) To be filled in | Ref. page of technical offer |
| --- | --- | --- | --- |
| Cable Type: | PROTOLON® (SMK) (N)TSKCGEWOEU with integrated optical fibers (LWL) |  |  |
| Conductor Structure: | 3 main power conductors: 3 × 25 mm² (stranded copper, FS category). |  |  |
|  | 2 grounding conductors: 2 × 25 mm² / 2 (split for symmetrical arrangement). |  |  |
|  | 1 optical fiber element: 1 × (6 LWL) for data transmission. |  |  |
| Rated Voltage: | 12/20kV |  |  |
| Maximum Permissible Voltage: | 24kV |  |  |
| Insulation: | High-quality EPR (Ethylene Propylene Rubber) with inner and outer semiconductive layers for electric field control. |  |  |
| Inner Sheath: | Polychloroprene (PCP). |  |  |
| Outer Sheath: | Double layer PCP rubber (type 5GM5), red color, oil-resistant, UV-resistant, ozone-resistant, flame-retardant. |  |  |
| Anti-twist Protection: | Textile braid between inner and outer sheath. |  |  |
| Resistance: | Operating temperature: -30 °C to +90 °C. |  |  |
|  | Short-circuit temperature: +250 °C. |  |  |
|  | Resistant to oil, UV, ozone. |  |  |
| Mechanical Properties: | Minimum bending radius: ≤ 5 × Ø (dynamic application) |  |  |
|  | Maximum reeling speed: up to 120 m/min |  |  |
|  | Maximum allowable tensile load: 15–20 N/mm² |  |  |
| Standards Required: | DIN VDE 0250-813, IEC 60228 |  |  |
| Tests: | Flame propagation IEC 60332-1-2 |  |  |
|  | Voltage test 29 kV for 5 minutes (VDE 0250-813) |  |  |

#### 2) Medium Voltage Cable 20 kV PRYSMIAN – PANZERFLEX ELX 3x35mm2+2x25mm2/2+6LWL 12/20KV, FIBEROPTICS MONOMODE 9/125

| Cable Specifications: |  | Compliance (YES/NO) To be filled in | Ref. page of technical offer |
| --- | --- | --- | --- |
| Cable Type: | ELX 3*35+2*25/2+6LWL |  |  |
| Conductor Structure: | 3 × 35 mm², stranded copper, class 5 (IEC 60228), tinned for corrosion resistance. |  |  |
|  | 2 × 25 mm² / 2 (split for symmetrical arrangement). |  |  |
|  | 6 monomode fibers 9/125 μm integrated in central element. |  |  |
| Rated Voltage: | 12/20kV |  |  |
| Maximum Permissible Voltage: | 24kV |  |  |
| Insulation: | High-quality EPR with semiconductive layers. |  |  |
| Inner Sheath: | Polychloroprene (PCP). |  |  |
| Outer Sheath: | Red PCP, resistant to UV, oil, chemicals, and flame. |  |  |
| Anti-twist Protection: | Textile braid between inner and outer sheath. |  |  |
| Resistance: | Operating temperature: -30 °C to +90 °C. |  |  |
|  | Short-circuit temperature: +250 °C. |  |  |
|  | Resistant to oil, UV, ozone, flame |  |  |
| Mechanical Properties: | Minimum bending radius: ≤ 8 × Ø |  |  |
|  | Maximum reeling speed: up to 180 m/min |  |  |
|  | Maximum tensile load: 15–20 N/mm² |  |  |
| Standards Required: | VDE 0250-813, IEC 60228, DIN VDE 0298, IEC 60332-1-2, IEC 60811-404 |  |  |
| Certifications: | CE, ISO 9001, ISO 14001 |  |  |
| Tests: | Flame propagation IEC 60332-1-2, |  |  |
|  | EMC performance EN 50081/50082 |  |  |
|  | Voltage test 29 kV for 5 minutes (VDE 0250-813) |  |  |

#### 3) Medium Voltage Cable 20 kV PANZERFLEX PROTOLON (SMK)-LWL (N)TSKCGEWOEU 3x25mm2+2x25mm2/2+1X(12E9LWL)

| Cable Specifications: |  | Compliance (YES/NO) To be filled in | Ref. page of technical offer |
| --- | --- | --- | --- |
| Cable Type: | PROTOLON (SMK)-LWL (N)TSKCGEWOEU 3*25+2*25/2+1X(12E9LWL) |  |  |
| Conductor Structure: | 3 × 25 mm², stranded copper, class 5 (IEC 60228), tinned for corrosion resistance. |  |  |
|  | 2 × 25 mm² / 2 (split for symmetrical arrangement). |  |  |
|  | 12 monomode fibers 9/125 μm integrated in central element. |  |  |
| Rated Voltage: | 12/20kV |  |  |
| Maximum Permissible Voltage: | 24kV |  |  |
| Insulation: | High-quality EPR with semiconductive layers. |  |  |
| Inner Sheath: | PCP rubber (type 5GM3). |  |  |
| Outer Sheath: | Double PCP layer, red color, UV, oil, and flame resistant (IEC 60332-1-2). |  |  |
| Anti-twist Protection: | Textile braid between inner and outer sheath. |  |  |
| Resistance: | Operating temperature: -30 °C to +90 °C. |  |  |
|  | Short-circuit temperature: +250 °C. |  |  |
|  | Resistant to oil, UV, ozone, flame |  |  |
| Mechanical Properties: | Minimum bending radius: ≤ 8 × Ø |  |  |
|  | Maximum reeling speed: up to 180 m/min |  |  |
|  | Maximum tensile load: 15–20 N/mm² |  |  |
| Standards Required: | VDE 0250-813, IEC 60228, DIN VDE 0298, IEC 60332-1-2, IEC 60811-404 |  |  |

### 4) Medium Voltage Cable 20 kV PANZERFLEX EL12/20KV 3x35mm2+2x25mm2/2+6FOX2.5/125

| Cable Specifications: |  | Compliance (YES/NO) To be filled in | Ref. page of technical offer |
| --- | --- | --- | --- |
| Cable Type: | EL12/20KV 3*35+2*25/2+6FOX2.5/125 |  |  |
| Conductor Structure: | 3 × 35 mm², stranded copper, class 5 (IEC 60228), tinned for corrosion resistance. |  |  |
|  | 2 × 25 mm² / 2 (split for symmetrical arrangement). |  |  |
|  | 6 monomode fibers 2.5/125 μm integrated in central element. |  |  |
| Rated Voltage: | 12/20kV |  |  |
| Maximum Permissible Voltage: | 24kV |  |  |
| Insulation: | High-quality EPR (Ethylene Propylene Rubber) with inner and outer semiconductive layers for electric field control. |  |  |
| Inner Sheath: | PCP rubber (type 5GM3). |  |  |
| Outer Sheath: | Double PCP layer, red color, UV, oil, and flame resistant (IEC 60332-1-2). |  |  |
| Anti-twist Protection: | Textile braid between inner and outer sheath. |  |  |
| Resistance: | Operating temperature: -30 °C to +90 °C. |  |  |
|  | Short-circuit temperature: +250 °C. |  |  |
|  | Resistant to oil, UV, ozone, flame |  |  |
| Mechanical Properties: | Minimum bending radius: ≤ 8 × Ø |  |  |
|  | Maximum reeling speed: up to 180 m/min |  |  |
|  | Maximum tensile load: 15–20 N/mm² |  |  |
| Standards Required: | VDE 0250-813, IEC 60228, DIN VDE 0298, IEC 60332-1-2, IEC 60811-404 |  |  |
| Certifications: | CE, ISO 9001, ISO 14001 |  |  |
| Tests: | Flame propagation IEC 60332-1-2, |  |  |
|  | EMC performance EN 50081/50082 |  |  |
|  | Voltage test 29 kV for 5 minutes (VDE 0250-813) |  |  |